## show
Pressure loss calculations
Summary
kinematic viscosity |  | Kv | 1 | mm2/s
specific weight |  | q | 1025 | kg/m3
Pressure loss before pump
|  | pump height above base | 1.5 | m |  | Suction flange
|  | liquid level | 4.9 | m |  | Or liquid level height above base, in case of tanks/waterline if drawn from overboard
|  | dp piping | 0 | bar |  | dp = differential pressure, which is pressure loss.
additional equipment losses: |  | dp xxx | 0 | bar
|  | dp xxx | 0 | bar
|  | dp xxx | 0 | bar
total system pressure loss |  | Pwr | 0 | mlc |  | Pressure loss
suction loss check: | NPSHa = Pa + Pz - Pd - Pwr |  | 12.9768 | mlc |  | NPSH available
| Pa |  | 10.0768 | mlc |  | Atmospheric pressure (101325 is standard number)
| Pz |  | 3.4 | mlc |  | Height pressure
| Pd |  | 0.5 | mlc | (water 38 C) | Vapour pressure of the liquid.
| added margin |  | 3 | mlc
| NPSHreq (minimal) |  | 9.9768 | mlc |  | NPSH required
Pressure loss after pump
|  | dp piping | 0 | bar
additional equipment losses: |  | dp xxx | 0 | bar
|  | dp xxx | 0 | bar
|  | dp xxx | 0 | bar
total system pressure loss |  | Pwr | 0 | mlc
|  | height | 0 | mlc
|  | Total | 0 | mlc
|  |  | 0 | bar

## total
IHC OFFSHORE & MARINE B.V.
Pressure loss calculations
YARD NR. :736 DRW NR. :736-000.00-xxx REV. NO. :0 DATE :11-3-2015
Summary
fill in values
kinematic viscosity |  | Kv | 1 | mm2/s
specific weight |  | q | 1025 | kg/m3
Pressure loss before pump
|  | pump height above base | 1.5 | m |  | Suction flange
|  | liquid level | 4.9 | m |  | Or liquid level height above base, in case of tanks/waterline if drawn from overboard
|  | dp piping | 0 | bar |  | dp = differential pressure, which is pressure loss.
additional equipment losses: |  | dp xxx | 0 | bar
|  | dp xxx | 0 | bar
|  | dp xxx | 0 | bar
total system pressure loss |  | Pwr | 0 | mlc |  | Pressure loss
suction loss check: | NPSHa = Pa + Pz - Pd - Pwr |  | 12.9768 | mlc |  | NPSH available
| Pa |  | 10.0768 | mlc |  | Atmospheric pressure (101325 is standard number)
| Pz |  | 3.4 | mlc |  | Height pressure
| Pd |  | 0.5 | mlc | (water 38 C) | Vapour pressure of the liquid.
| added margin |  | 3 | mlc
| NPSHreq (minimal) |  | 9.9768 | mlc |  | NPSH required
Pressure loss after pump
|  | dp piping | 0 | bar
additional equipment losses: |  | dp xxx | 0 | bar
|  | dp xxx | 0 | bar
|  | dp xxx | 0 | bar
total system pressure loss |  | Pwr | 0 | mlc
|  | height | 0 | mlc
|  | Total | 0 | mlc
|  |  | 0 | bar

## Parameters
| Suction side | [15 empty] | Pressure side
DN | 500 | 450 | 400 | 350 | 300 | 250 | 200 | 150 | 125 | 100 | 80 | 65 | 50 | 40 | 32 | 25 | 500 | 450 | 400 | 350 | 300 | 250 | 200 | 150 | 125 | 100 | 80 | 65 | 50 | 40 | 32 | 25
Q = flow of liquid in m3/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
L = length of straight pipe in m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
M = material of pipe (1=steel , 2=non steel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
pipe dimension (1=normal(C100), 2=heavy(C105), 3=extra(C110)) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
check vlv
but fl vlv
globe valve
flow reg. vlv
gate valve
branch 180g*
branch 90g**
bend 90 gr
diverter
reducer
inlet
filter
bellow
* a branch 180g is where the liquid passes a branch
** a branch 90g is where the liquid takes the branch

## DN500 S
Calculation pressure loss in liquid pipelines
fill in values
Q = flow of liquid in m3/h |  |  |  | 0 | m3/h
q = specific weight of liquid in kg/m3 |  |  |  | 1025 | kg/m3
Kv = kinematic viscosity in cst |  |  |  | 1 | cst-mm2/s
L = length of straight pipe in m |  |  |  | 0 | m
D = diameter inside in mm |  |  |  | 450 | mm | DN | 450 |  | pipe dimension: | 0 | 1=normal(C100), 2=heavy(C105), 3=extra(C110)
M = material of pipe (1=steel , 2=non steel) |  |  |  | 0 |  | k st | 0.15 | mm | k pvc | 0.02 | mm
S = total of resistant value |  |  |  | 0
Result of calculation :
Velocity : |  |  | V = Q / 3600 / 0.785 x D x D = |  |  |  | 0 | m/sec
Reynolds nr :(>2320 = turb.flow) |  |  | Re = V x D / Kv = |  |  |  | 0 | 0
k/d | [6 empty] | 0.00033333
Re.k/d | [6 empty] | 0
Resistant coefficient :(Laminar flow) |  |  | y = 64 / Re = |  |  |  | 0
Resistant coefficient :(Turb. flow) |  |  | y = 0.0055(1+(20000k/D+10^6/Re)^1/3 = |  |  |  | 0
Diff.pressure : |  |  | Dp = (yxL/D+S)xqxVxV/(2x100000) = |  |  |  | 0 | bar | p=rho*g*H
[7 empty] | 0 | m.w.c. | H=p/(rho*g)
check |  |  | hydraulisch glad |  |  |  | ruw |  |  |  | overgangsgebied
|  |  | Re.k/d<65 |  | Re |  | Re.k/d>1300 |  |  |  | 65<Re.k/d<1300
y
|  | 4.58a | #DIV/0! | Blasius | <1e5 | 4.59a | 0.015263 | Nikuradse |  | 4.60 | #DIV/0!
|  | 4.58b | #DIV/0! | Nikuradse | 1e5-5e6 | 4.59b | 0.0159 | Moody
|  | 4.58d | #DIV/0! | Hermann | <2e6
S | amount | zeta | zeta total |  | remark
check vlv | 0 | 5 | 0
but fl vlv | 0 | 0.5 | 0
globe valve | 0 | 4 | 0
flow reg. vlv | 0 | 5 | 0
gate valve | 0 | 0.5 | 0
branch 180g | 0 | 0.5 | 0
branch 90g | 0 | 1 | 0
bend 90 gr | 0 | 3.5 | 0 |  | laminar: 3,5 - turbulent: 0,35
diverter | 0 | 1 | 0
reducer | 0 | 0.1 | 0
inlet | 0 | 1 | 0
filter | 0 | 6 | 0
bellow | 0 | 0.2 | 0
total |  |  | 0

## DN450 S
Calculation pressure loss in liquid pipelines
fill in values
Q = flow of liquid in m3/h |  |  |  | 0 | m3/h
q = specific weight of liquid in kg/m3 |  |  |  | 1025 | kg/m3
Kv = kinematic viscosity in cst |  |  |  | 1 | cst-mm2/s
L = length of straight pipe in m |  |  |  | 0 | m
D = diameter inside in mm |  |  |  | 450 | mm | DN | 450 |  | pipe dimension: | 0 | 1=normal(C100), 2=heavy(C105), 3=extra(C110)
M = material of pipe (1=steel , 2=non steel) |  |  |  | 0 |  | k st | 0.15 | mm | k pvc | 0.02 | mm
S = total of resistant value |  |  |  | 0
Result of calculation :
Velocity : |  |  | V = Q / 3600 / 0.785 x D x D = |  |  |  | 0 | m/sec
Reynolds nr :(>2320 = turb.flow) |  |  | Re = V x D / Kv = |  |  |  | 0 | 0
k/d | [6 empty] | 0.00033333
Re.k/d | [6 empty] | 0
Resistant coefficient :(Laminar flow) |  |  | y = 64 / Re = |  |  |  | 0
Resistant coefficient :(Turb. flow) |  |  | y = 0.0055(1+(20000k/D+10^6/Re)^1/3 = |  |  |  | 0
Diff.pressure : |  |  | Dp = (yxL/D+S)xqxVxV/(2x100000) = |  |  |  | 0 | bar | p=rho*g*H
[7 empty] | 0 | m.w.c. | H=p/(rho*g)
check |  |  | hydraulisch glad |  |  |  | ruw |  |  |  | overgangsgebied
|  |  | Re.k/d<65 |  | Re |  | Re.k/d>1300 |  |  |  | 65<Re.k/d<1300
y
|  | 4.58a | #DIV/0! | Blasius | <1e5 | 4.59a | 0.015263 | Nikuradse |  | 4.60 | #DIV/0!
|  | 4.58b | #DIV/0! | Nikuradse | 1e5-5e6 | 4.59b | 0.0159 | Moody
|  | 4.58d | #DIV/0! | Hermann | <2e6
S | amount | zeta | zeta total |  | remark
check vlv | 0 | 5 | 0
but fl vlv | 0 | 0.5 | 0
globe valve | 0 | 4 | 0
flow reg. vlv | 0 | 5 | 0
gate valve | 0 | 0.5 | 0
branch 180g | 0 | 0.5 | 0
branch 90g | 0 | 1 | 0
bend 90 gr | 0 | 3.5 | 0 |  | laminar: 3,5 - turbulent: 0,35
diverter | 0 | 1 | 0
reducer | 0 | 0.1 | 0
inlet | 0 | 1 | 0
filter | 0 | 6 | 0
bellow | 0 | 0.2 | 0
total |  |  | 0

## DN400 S
Calculation pressure loss in liquid pipelines
fill in values
Q = flow of liquid in m3/h |  |  |  | 0 | m3/h
q = specific weight of liquid in kg/m3 |  |  |  | 1025 | kg/m3
Kv = kinematic viscosity in cst |  |  |  | 1 | cst-mm2/s
L = length of straight pipe in m |  |  |  | 0 | m
D = diameter inside in mm |  |  |  | 400 | mm | DN | 400 |  | pipe dimension: | 0 | 1=normal(C100), 2=heavy(C105), 3=extra(C110)
M = material of pipe (1=steel , 2=non steel) |  |  |  | 0 |  | k st | 0.15 | mm | k pvc | 0.02 | mm
S = total of resistant value |  |  |  | 0
Result of calculation :
Velocity : |  |  | V = Q / 3600 / 0.785 x D x D = |  |  |  | 0 | m/sec
Reynolds nr :(>2320 = turb.flow) |  |  | Re = V x D / Kv = |  |  |  | 0 | 0
k/d | [6 empty] | 0.000375
Re.k/d | [6 empty] | 0
Resistant coefficient :(Laminar flow) |  |  | y = 64 / Re = |  |  |  | 0
Resistant coefficient :(Turb. flow) |  |  | y = 0.0055(1+(20000k/D+10^6/Re)^1/3 = |  |  |  | 0
Diff.pressure : |  |  | Dp = (yxL/D+S)xqxVxV/(2x100000) = |  |  |  | 0 | bar | p=rho*g*H
[7 empty] | 0 | m.w.c. | H=p/(rho*g)
check |  |  | hydraulisch glad |  |  |  | ruw |  |  |  | overgangsgebied
|  |  | Re.k/d<65 |  | Re |  | Re.k/d>1300 |  |  |  | 65<Re.k/d<1300
y
|  | 4.58a | #DIV/0! | Blasius | <1e5 | 4.59a | 0.015657 | Nikuradse |  | 4.60 | #DIV/0!
|  | 4.58b | #DIV/0! | Nikuradse | 1e5-5e6 | 4.59b | 0.016317 | Moody
|  | 4.58d | #DIV/0! | Hermann | <2e6
S | amount | zeta | zeta total |  | remark
check vlv | 0 | 5 | 0
but fl vlv | 0 | 0.5 | 0
globe valve | 0 | 4 | 0
flow reg. vlv | 0 | 5 | 0
gate valve | 0 | 0.5 | 0
branch 180g | 0 | 0.5 | 0
branch 90g | 0 | 1 | 0
bend 90 gr | 0 | 3.5 | 0 |  | laminar: 3,5 - turbulent: 0,35
diverter | 0 | 1 | 0
reducer | 0 | 0.1 | 0
inlet | 0 | 1 | 0
filter | 0 | 6 | 0
bellow | 0 | 0.2 | 0
total |  |  | 0

## DN350 S
Calculation pressure loss in liquid pipelines
fill in values
Q = flow of liquid in m3/h |  |  |  | 0 | m3/h
q = specific weight of liquid in kg/m3 |  |  |  | 1025 | kg/m3
Kv = kinematic viscosity in cst |  |  |  | 1 | cst-mm2/s
L = length of straight pipe in m |  |  |  | 0 | m
D = diameter inside in mm |  |  |  | 350 | mm | DN | 350 |  | pipe dimension: | 0 | 1=normal(C100), 2=heavy(C105), 3=extra(C110)
M = material of pipe (1=steel , 2=non steel) |  |  |  | 0 |  | k st | 0.15 | mm | k pvc | 0.02 | mm
S = total of resistant value |  |  |  | 0
Result of calculation :
Velocity : |  |  | V = Q / 3600 / 0.785 x D x D = |  |  |  | 0 | m/sec
Reynolds nr :(>2320 = turb.flow) |  |  | Re = V x D / Kv = |  |  |  | 0 | 0
k/d | [6 empty] | 0.00042857
Re.k/d | [6 empty] | 0
Resistant coefficient :(Laminar flow) |  |  | y = 64 / Re = |  |  |  | 0
Resistant coefficient :(Turb. flow) |  |  | y = 0.0055(1+(20000k/D+10^6/Re)^1/3 = |  |  |  | 0
Diff.pressure : |  |  | Dp = (yxL/D+S)xqxVxV/(2x100000) = |  |  |  | 0 | bar | p=rho*g*H
[7 empty] | 0 | m.w.c. | H=p/(rho*g)
check |  |  | hydraulisch glad |  |  |  | ruw |  |  |  | overgangsgebied
|  |  | Re.k/d<65 |  | Re |  | Re.k/d>1300 |  |  |  | 65<Re.k/d<1300
y
|  | 4.58a | #DIV/0! | Blasius | <1e5 | 4.59a | 0.016121 | Nikuradse |  | 4.60 | #DIV/0!
|  | 4.58b | #DIV/0! | Nikuradse | 1e5-5e6 | 4.59b | 0.016809 | Moody
|  | 4.58d | #DIV/0! | Hermann | <2e6
S | amount | zeta | zeta total |  | remark
check vlv | 0 | 5 | 0
but fl vlv | 0 | 0.5 | 0
globe valve | 0 | 4 | 0
flow reg. vlv | 0 | 5 | 0
gate valve | 0 | 0.5 | 0
branch 180g | 0 | 0.5 | 0
branch 90g | 0 | 1 | 0
bend 90 gr | 0 | 3.5 | 0 |  | laminar: 3,5 - turbulent: 0,35
diverter | 0 | 1 | 0
reducer | 0 | 0.1 | 0
inlet | 0 | 1 | 0
filter | 0 | 6 | 0
bellow | 0 | 0.2 | 0
total |  |  | 0

## DN300 S
Calculation pressure loss in liquid pipelines
fill in values
Q = flow of liquid in m3/h |  |  |  | 0 | m3/h
q = specific weight of liquid in kg/m3 |  |  |  | 1025 | kg/m3
Kv = kinematic viscosity in cst |  |  |  | 1 | cst-mm2/s
L = length of straight pipe in m |  |  |  | 0 | m
D = diameter inside in mm |  |  |  | 300 | mm | DN | 300 |  | pipe dimension: | 0 | 1=normal(C100), 2=heavy(C105), 3=extra(C110)
M = material of pipe (1=steel , 2=non steel) |  |  |  | 0 |  | k st | 0.15 | mm | k pvc | 0.02 | mm
S = total of resistant value |  |  |  | 0
Result of calculation :
Velocity : |  |  | V = Q / 3600 / 0.785 x D x D = |  |  |  | 0 | m/sec
Reynolds nr :(>2320 = turb.flow) |  |  | Re = V x D / Kv = |  |  |  | 0 | 0
k/d | [6 empty] | 0.0005
Re.k/d | [6 empty] | 0
Resistant coefficient :(Laminar flow) |  |  | y = 64 / Re = |  |  |  | 0
Resistant coefficient :(Turb. flow) |  |  | y = 0.0055(1+(20000k/D+10^6/Re)^1/3 = |  |  |  | 0
Diff.pressure : |  |  | Dp = (yxL/D+S)xqxVxV/(2x100000) = |  |  |  | 0 | bar | p=rho*g*H
[7 empty] | 0 | m.w.c. | H=p/(rho*g)
check |  |  | hydraulisch glad |  |  |  | ruw |  |  |  | overgangsgebied
|  |  | Re.k/d<65 |  | Re |  | Re.k/d>1300 |  |  |  | 65<Re.k/d<1300
y
|  | 4.58a | #DIV/0! | Blasius | <1e5 | 4.59a | 0.016683 | Nikuradse |  | 4.60 | #DIV/0!
|  | 4.58b | #DIV/0! | Nikuradse | 1e5-5e6 | 4.59b | 0.017406 | Moody
|  | 4.58d | #DIV/0! | Hermann | <2e6
S | amount | zeta | zeta total |  | remark
check vlv | 0 | 5 | 0
but fl vlv | 0 | 0.5 | 0
globe valve | 0 | 4 | 0
flow reg. vlv | 0 | 5 | 0
gate valve | 0 | 0.5 | 0
branch 180g | 0 | 0.5 | 0
branch 90g | 0 | 1 | 0
bend 90 gr | 0 | 3.5 | 0 |  | laminar: 3,5 - turbulent: 0,35
diverter | 0 | 1 | 0
reducer | 0 | 0.1 | 0
inlet | 0 | 1 | 0
filter | 0 | 6 | 0
bellow | 0 | 0.2 | 0
total |  |  | 0

## DN250 S
Calculation pressure loss in liquid pipelines
fill in values
Q = flow of liquid in m3/h |  |  |  | 0 | m3/h
q = specific weight of liquid in kg/m3 |  |  |  | 1025 | kg/m3
Kv = kinematic viscosity in cst |  |  |  | 1 | cst-mm2/s
L = length of straight pipe in m |  |  |  | 0 | m
D = diameter inside in mm |  |  |  | 250 | mm | DN | 250 |  | pipe dimension: | 0 | 1=normal(C100), 2=heavy(C105), 3=extra(C110)
M = material of pipe (1=steel , 2=non steel) |  |  |  | 0 |  | k st | 0.15 | mm | k pvc | 0.02 | mm
S = total of resistant value |  |  |  | 0
Result of calculation :
Velocity : |  |  | V = Q / 3600 / 0.785 x D x D = |  |  |  | 0 | m/sec
Reynolds nr :(>2320 = turb.flow) |  |  | Re = V x D / Kv = |  |  |  | 0 | 0
k/d | [6 empty] | 0.0006
Re.k/d | [6 empty] | 0
Resistant coefficient :(Laminar flow) |  |  | y = 64 / Re = |  |  |  | 0
Resistant coefficient :(Turb. flow) |  |  | y = 0.0055(1+(20000k/D+10^6/Re)^1/3 = |  |  |  | 0
Diff.pressure : |  |  | Dp = (yxL/D+S)xqxVxV/(2x100000) = |  |  |  | 0 | bar | p=rho*g*H
[7 empty] | 0 | m.w.c. | H=p/(rho*g)
check |  |  | hydraulisch glad |  |  |  | ruw |  |  |  | overgangsgebied
|  |  | Re.k/d<65 |  | Re |  | Re.k/d>1300 |  |  |  | 65<Re.k/d<1300
y
|  | 4.58a | #DIV/0! | Blasius | <1e5 | 4.59a | 0.017388 | Nikuradse |  | 4.60 | #DIV/0!
|  | 4.58b | #DIV/0! | Nikuradse | 1e5-5e6 | 4.59b | 0.018151 | Moody
|  | 4.58d | #DIV/0! | Hermann | <2e6
S | amount | zeta | zeta total |  | remark
check vlv | 0 | 5 | 0
but fl vlv | 0 | 0.5 | 0
globe valve | 0 | 4 | 0
flow reg. vlv | 0 | 5 | 0
gate valve | 0 | 0.5 | 0
branch 180g | 0 | 0.5 | 0
branch 90g | 0 | 1 | 0
bend 90 gr | 0 | 3.5 | 0 |  | laminar: 3,5 - turbulent: 0,35
diverter | 0 | 1 | 0
reducer | 0 | 0.1 | 0
inlet | 0 | 1 | 0
filter | 0 | 6 | 0
bellow | 0 | 0.2 | 0
total |  |  | 0

## DN200 S
Calculation pressure loss in liquid pipelines
fill in values
Q = flow of liquid in m3/h |  |  |  | 0 | m3/h
q = specific weight of liquid in kg/m3 |  |  |  | 1025 | kg/m3
Kv = kinematic viscosity in cst |  |  |  | 1 | cst-mm2/s
L = length of straight pipe in m |  |  |  | 0 | m
D = diameter inside in mm |  |  |  | 200 | mm | DN | 200 |  | pipe dimension: | 0 | 1=normal(C100), 2=heavy(C105), 3=extra(C110)
M = material of pipe (1=steel , 2=non steel) |  |  |  | 0 |  | k st | 0.15 | mm | k pvc | 0.02 | mm
S = total of resistant value |  |  |  | 0
Result of calculation :
Velocity : |  |  | V = Q / 3600 / 0.785 x D x D = |  |  |  | 0 | m/sec
Reynolds nr :(>2320 = turb.flow) |  |  | Re = V x D / Kv = |  |  |  | 0 | 0
k/d | [6 empty] | 0.00075
Re.k/d | [6 empty] | 0
Resistant coefficient :(Laminar flow) |  |  | y = 64 / Re = |  |  |  | 0
Resistant coefficient :(Turb. flow) |  |  | y = 0.0055(1+(20000k/D+10^6/Re)^1/3 = |  |  |  | 0
Diff.pressure : |  |  | Dp = (yxL/D+S)xqxVxV/(2x100000) = |  |  |  | 0 | bar | p=rho*g*H
[7 empty] | 0 | m.w.c. | H=p/(rho*g)
check |  |  | hydraulisch glad |  |  |  | ruw |  |  |  | overgangsgebied
|  |  | Re.k/d<65 |  | Re |  | Re.k/d>1300 |  |  |  | 65<Re.k/d<1300
y
|  | 4.58a | #DIV/0! | Blasius | <1e5 | 4.59a | 0.018312 | Nikuradse |  | 4.60 | #DIV/0!
|  | 4.58b | #DIV/0! | Nikuradse | 1e5-5e6 | 4.59b | 0.019128 | Moody
|  | 4.58d | #DIV/0! | Hermann | <2e6
S | amount | zeta | zeta total |  | remark
check vlv | 0 | 5 | 0
but fl vlv | 0 | 0.5 | 0
globe valve | 0 | 4 | 0
flow reg. vlv | 0 | 5 | 0
gate valve | 0 | 0.5 | 0
branch 180g | 0 | 0.5 | 0
branch 90g | 0 | 1 | 0
bend 90 gr | 0 | 3.5 | 0 |  | laminar: 3,5 - turbulent: 0,35
diverter | 0 | 1 | 0
reducer | 0 | 0.1 | 0
inlet | 0 | 1 | 0
filter | 0 | 6 | 0
bellow | 0 | 0.2 | 0
total |  |  | 0

## DN150 S
Calculation pressure loss in liquid pipelines
fill in values
Q = flow of liquid in m3/h |  |  |  | 0 | m3/h
q = specific weight of liquid in kg/m3 |  |  |  | 1025 | kg/m3
Kv = kinematic viscosity in cst |  |  |  | 1 | cst-mm2/s
L = length of straight pipe in m |  |  |  | 0 | m
D = diameter inside in mm |  |  |  | 150 | mm | DN | 150 |  | pipe dimension: | 0 | 1=normal(C100), 2=heavy(C105), 3=extra(C110)
M = material of pipe (1=steel , 2=non steel) |  |  |  | 0 |  | k st | 0.15 | mm | k pvc | 0.02 | mm
S = total of resistant value |  |  |  | 0
Result of calculation :
Velocity : |  |  | V = Q / 3600 / 0.785 x D x D = |  |  |  | 0 | m/sec
Reynolds nr :(>2320 = turb.flow) |  |  | Re = V x D / Kv = |  |  |  | 0 | 0
k/d | [6 empty] | 0.001
Re.k/d | [6 empty] | 0
Resistant coefficient :(Laminar flow) |  |  | y = 64 / Re = |  |  |  | 0
Resistant coefficient :(Turb. flow) |  |  | y = 0.0055(1+(20000k/D+10^6/Re)^1/3 = |  |  |  | 0
Diff.pressure : |  |  | Dp = (yxL/D+S)xqxVxV/(2x100000) = |  |  |  | 0 | bar | p=rho*g*H
[7 empty] | 0 | m.w.c. | H=p/(rho*g)
check |  |  | hydraulisch glad |  |  |  | ruw |  |  |  | overgangsgebied
|  |  | Re.k/d<65 |  | Re |  | Re.k/d>1300 |  |  |  | 65<Re.k/d<1300
y
|  | 4.58a | #DIV/0! | Blasius | <1e5 | 4.59a | 0.019616 | Nikuradse |  | 4.60 | #DIV/0!
|  | 4.58b | #DIV/0! | Nikuradse | 1e5-5e6 | 4.59b | 0.0205 | Moody
|  | 4.58d | #DIV/0! | Hermann | <2e6
S | amount | zeta | zeta total |  | remark
check vlv | 0 | 5 | 0
but fl vlv | 0 | 0.5 | 0
globe valve | 0 | 4 | 0
flow reg. vlv | 0 | 5 | 0
gate valve | 0 | 0.5 | 0
branch 180g | 0 | 0.5 | 0
branch 90g | 0 | 1 | 0
bend 90 gr | 0 | 3.5 | 0 |  | laminar: 3,5 - turbulent: 0,35
diverter | 0 | 1 | 0
reducer | 0 | 0.1 | 0
inlet | 0 | 1 | 0
filter | 0 | 6 | 0
bellow | 0 | 0.2 | 0
total |  |  | 0

## DN125 S
Calculation pressure loss in liquid pipelines
fill in values
Q = flow of liquid in m3/h |  |  |  | 0 | m3/h
q = specific weight of liquid in kg/m3 |  |  |  | 1025 | kg/m3
Kv = kinematic viscosity in cst |  |  |  | 1 | cst-mm2/s
L = length of straight pipe in m |  |  |  | 0 | m
D = diameter inside in mm |  |  |  | 125 | mm | DN | 125 |  | pipe dimension: | 0 | 1=normal(C100), 2=heavy(C105), 3=extra(C110)
M = material of pipe (1=steel , 2=non steel) |  |  |  | 0 |  | k st | 0.15 | mm | k pvc | 0.02 | mm
S = total of resistant value |  |  |  | 0
Result of calculation :
Velocity : |  |  | V = Q / 3600 / 0.785 x D x D = |  |  |  | 0 | m/sec
Reynolds nr :(>2320 = turb.flow) |  |  | Re = V x D / Kv = |  |  |  | 0 | 0
k/d | [6 empty] | 0.0012
Re.k/d | [6 empty] | 0
Resistant coefficient :(Laminar flow) |  |  | y = 64 / Re = |  |  |  | 0
Resistant coefficient :(Turb. flow) |  |  | y = 0.0055(1+(20000k/D+10^6/Re)^1/3 = |  |  |  | 0
Diff.pressure : |  |  | Dp = (yxL/D+S)xqxVxV/(2x100000) = |  |  |  | 0 | bar | p=rho*g*H
[7 empty] | 0 | m.w.c. | H=p/(rho*g)
check |  |  | hydraulisch glad |  |  |  | ruw |  |  |  | overgangsgebied
|  |  | Re.k/d<65 |  | Re |  | Re.k/d>1300 |  |  |  | 65<Re.k/d<1300
y
|  | 4.58a | #DIV/0! | Blasius | <1e5 | 4.59a | 0.020516 | Nikuradse |  | 4.60 | #DIV/0!
|  | 4.58b | #DIV/0! | Nikuradse | 1e5-5e6 | 4.59b | 0.02144 | Moody
|  | 4.58d | #DIV/0! | Hermann | <2e6
S | amount | zeta | zeta total |  | remark
check vlv | 0 | 5 | 0
but fl vlv | 0 | 0.5 | 0
globe valve | 0 | 4 | 0
flow reg. vlv | 0 | 5 | 0
gate valve | 0 | 0.5 | 0
branch 180g | 0 | 0.5 | 0
branch 90g | 0 | 1 | 0
bend 90 gr | 0 | 3.5 | 0 |  | laminar: 3,5 - turbulent: 0,35
diverter | 0 | 1 | 0
reducer | 0 | 0.1 | 0
inlet | 0 | 1 | 0
filter | 0 | 6 | 0
bellow | 0 | 0.2 | 0
total |  |  | 0

## DN100 S
Calculation pressure loss in liquid pipelines
fill in values
Q = flow of liquid in m3/h |  |  |  | 0 | m3/h
q = specific weight of liquid in kg/m3 |  |  |  | 1025 | kg/m3
Kv = kinematic viscosity in cst |  |  |  | 1 | cst-mm2/s
L = length of straight pipe in m |  |  |  | 0 | m
D = diameter inside in mm |  |  |  | 100 | mm | DN | 100 |  | pipe dimension: | 0 | 1=normal(C100), 2=heavy(C105), 3=extra(C110)
M = material of pipe (1=steel , 2=non steel) |  |  |  | 0 |  | k st | 0.15 | mm | k pvc | 0.02 | mm
S = total of resistant value |  |  |  | 0
Result of calculation :
Velocity : |  |  | V = Q / 3600 / 0.785 x D x D = |  |  |  | 0 | m/sec
Reynolds nr :(>2320 = turb.flow) |  |  | Re = V x D / Kv = |  |  |  | 0 | 0
k/d | [6 empty] | 0.0015
Re.k/d | [6 empty] | 0
Resistant coefficient :(Laminar flow) |  |  | y = 64 / Re = |  |  |  | 0
Resistant coefficient :(Turb. flow) |  |  | y = 0.0055(1+(20000k/D+10^6/Re)^1/3 = |  |  |  | 0
Diff.pressure : |  |  | Dp = (yxL/D+S)xqxVxV/(2x100000) = |  |  |  | 0 | bar | p=rho*g*H
[7 empty] | 0 | m.w.c. | H=p/(rho*g)
check |  |  | hydraulisch glad |  |  |  | ruw |  |  |  | overgangsgebied
|  |  | Re.k/d<65 |  | Re |  | Re.k/d>1300 |  |  |  | 65<Re.k/d<1300
y
|  | 4.58a | #DIV/0! | Blasius | <1e5 | 4.59a | 0.021704 | Nikuradse |  | 4.60 | #DIV/0!
|  | 4.58b | #DIV/0! | Nikuradse | 1e5-5e6 | 4.59b | 0.022671 | Moody
|  | 4.58d | #DIV/0! | Hermann | <2e6
S | amount | zeta | zeta total |  | remark
check vlv | 0 | 5 | 0
but fl vlv | 0 | 0.5 | 0
globe valve | 0 | 4 | 0
flow reg. vlv | 0 | 5 | 0
gate valve | 0 | 0.5 | 0
branch 180g | 0 | 0.5 | 0
branch 90g | 0 | 1 | 0
bend 90 gr | 0 | 3.5 | 0 |  | laminar: 3,5 - turbulent: 0,35
diverter | 0 | 1 | 0
reducer | 0 | 0.1 | 0
inlet | 0 | 1 | 0
filter | 0 | 6 | 0
bellow | 0 | 0.2 | 0
total |  |  | 0

## DN80 S
Calculation pressure loss in liquid pipelines
fill in values
Q = flow of liquid in m3/h |  |  |  | 0 | m3/h
q = specific weight of liquid in kg/m3 |  |  |  | 1025 | kg/m3
Kv = kinematic viscosity in cst |  |  |  | 1 | cst-mm2/s
L = length of straight pipe in m |  |  |  | 0 | m
D = diameter inside in mm |  |  |  | 80 | mm | DN | 80 |  | pipe dimension: | 0 | 1=normal(C100), 2=heavy(C105), 3=extra(C110)
M = material of pipe (1=steel , 2=non steel) |  |  |  | 0 |  | k st | 0.15 | mm | k pvc | 0.02 | mm
S = total of resistant value |  |  |  | 0
Result of calculation :
Velocity : |  |  | V = Q / 3600 / 0.785 x D x D = |  |  |  | 0 | m/sec
Reynolds nr :(>2320 = turb.flow) |  |  | Re = V x D / Kv = |  |  |  | 0 | 0
k/d | [6 empty] | 0.001875
Re.k/d | [6 empty] | 0
Resistant coefficient :(Laminar flow) |  |  | y = 64 / Re = |  |  |  | 0
Resistant coefficient :(Turb. flow) |  |  | y = 0.0055(1+(20000k/D+10^6/Re)^1/3 = |  |  |  | 0
Diff.pressure : |  |  | Dp = (yxL/D+S)xqxVxV/(2x100000) = |  |  |  | 0 | bar | p=rho*g*H
[7 empty] | 0 | m.w.c. | H=p/(rho*g)
check |  |  | hydraulisch glad |  |  |  | ruw |  |  |  | overgangsgebied
|  |  | Re.k/d<65 |  | Re |  | Re.k/d>1300 |  |  |  | 65<Re.k/d<1300
y
|  | 4.58a | #DIV/0! | Blasius | <1e5 | 4.59a | 0.022999 | Nikuradse |  | 4.60 | #DIV/0!
|  | 4.58b | #DIV/0! | Nikuradse | 1e5-5e6 | 4.59b | 0.023997 | Moody
|  | 4.58d | #DIV/0! | Hermann | <2e6
S | amount | zeta | zeta total |  | remark
check vlv | 0 | 5 | 0
but fl vlv | 0 | 0.5 | 0
globe valve | 0 | 4 | 0
flow reg. vlv | 0 | 5 | 0
gate valve | 0 | 0.5 | 0
branch 180g | 0 | 0.5 | 0
branch 90g | 0 | 1 | 0
bend 90 gr | 0 | 3.5 | 0 |  | laminar: 3,5 - turbulent: 0,35
diverter | 0 | 1 | 0
reducer | 0 | 0.1 | 0
inlet | 0 | 1 | 0
filter | 0 | 6 | 0
bellow | 0 | 0.2 | 0
total |  |  | 0

## DN65 S
Calculation pressure loss in liquid pipelines
fill in values
Q = flow of liquid in m3/h |  |  |  | 0 | m3/h
q = specific weight of liquid in kg/m3 |  |  |  | 1025 | kg/m3
Kv = kinematic viscosity in cst |  |  |  | 1 | cst-mm2/s
L = length of straight pipe in m |  |  |  | 0 | m
D = diameter inside in mm |  |  |  | 65 | mm | DN | 65 |  | pipe dimension: | 0 | 1=normal(C100), 2=heavy(C105), 3=extra(C110)
M = material of pipe (1=steel , 2=non steel) |  |  |  | 0 |  | k st | 0.15 | mm | k pvc | 0.02 | mm
S = total of resistant value |  |  |  | 0
Result of calculation :
Velocity : |  |  | V = Q / 3600 / 0.785 x D x D = |  |  |  | 0 | m/sec
Reynolds nr :(>2320 = turb.flow) |  |  | Re = V x D / Kv = |  |  |  | 0 | 0
k/d | [6 empty] | 0.0023077
Re.k/d | [6 empty] | 0
Resistant coefficient :(Laminar flow) |  |  | y = 64 / Re = |  |  |  | 0
Resistant coefficient :(Turb. flow) |  |  | y = 0.0055(1+(20000k/D+10^6/Re)^1/3 = |  |  |  | 0
Diff.pressure : |  |  | Dp = (yxL/D+S)xqxVxV/(2x100000) = |  |  |  | 0 | bar | p=rho*g*H
[7 empty] | 0 | m.w.c. | H=p/(rho*g)
check |  |  | hydraulisch glad |  |  |  | ruw |  |  |  | overgangsgebied
|  |  | Re.k/d<65 |  | Re |  | Re.k/d>1300 |  |  |  | 65<Re.k/d<1300
y
|  | 4.58a | #DIV/0! | Blasius | <1e5 | 4.59a | 0.02431 | Nikuradse |  | 4.60 | #DIV/0!
|  | 4.58b | #DIV/0! | Nikuradse | 1e5-5e6 | 4.59b | 0.025322 | Moody
|  | 4.58d | #DIV/0! | Hermann | <2e6
S | amount | zeta | zeta total |  | remark
check vlv | 0 | 5 | 0
but fl vlv | 0 | 0.5 | 0
globe valve | 0 | 4 | 0
flow reg. vlv | 0 | 5 | 0
gate valve | 0 | 0.5 | 0
branch 180g | 0 | 0.5 | 0
branch 90g | 0 | 1 | 0
bend 90 gr | 0 | 3.5 | 0 |  | laminar: 3,5 - turbulent: 0,35
diverter | 0 | 1 | 0
reducer | 0 | 0.1 | 0
inlet | 0 | 1 | 0
filter | 0 | 6 | 0
bellow | 0 | 0.2 | 0
total |  |  | 0

## DN50 S
Calculation pressure loss in liquid pipelines
fill in values
Q = flow of liquid in m3/h |  |  |  | 0 | m3/h
q = specific weight of liquid in kg/m3 |  |  |  | 1025 | kg/m3
Kv = kinematic viscosity in cst |  |  |  | 1 | cst-mm2/s
L = length of straight pipe in m |  |  |  | 0 | m
D = diameter inside in mm |  |  |  | 50 | mm | DN | 50 |  | pipe dimension: | 0 | 1=normal(C100), 2=heavy(C105), 3=extra(C110)
M = material of pipe (1=steel , 2=non steel) |  |  |  | 0 |  | k st | 0.15 | mm | k pvc | 0.02 | mm
S = total of resistant value |  |  |  | 0
Result of calculation :
Velocity : |  |  | V = Q / 3600 / 0.785 x D x D = |  |  |  | 0 | m/sec
Reynolds nr :(>2320 = turb.flow) |  |  | Re = V x D / Kv = |  |  |  | 0 | 0
k/d | [6 empty] | 0.003
Re.k/d | [6 empty] | 0
Resistant coefficient :(Laminar flow) |  |  | y = 64 / Re = |  |  |  | 0
Resistant coefficient :(Turb. flow) |  |  | y = 0.0055(1+(20000k/D+10^6/Re)^1/3 = |  |  |  | 0
Diff.pressure : |  |  | Dp = (yxL/D+S)xqxVxV/(2x100000) = |  |  |  | 0 | bar | p=rho*g*H
[7 empty] | 0 | m.w.c. | H=p/(rho*g)
check |  |  | hydraulisch glad |  |  |  | ruw |  |  |  | overgangsgebied
|  |  | Re.k/d<65 |  | Re |  | Re.k/d>1300 |  |  |  | 65<Re.k/d<1300
y
|  | 4.58a | #DIV/0! | Blasius | <1e5 | 4.59a | 0.026135 | Nikuradse |  | 4.60 | #DIV/0!
|  | 4.58b | #DIV/0! | Nikuradse | 1e5-5e6 | 4.59b | 0.027134 | Moody
|  | 4.58d | #DIV/0! | Hermann | <2e6
S | amount | zeta | zeta total |  | remark
check vlv | 0 | 5 | 0
but fl vlv | 0 | 0.5 | 0
globe valve | 0 | 4 | 0
flow reg. vlv | 0 | 5 | 0
gate valve | 0 | 0.5 | 0
branch 180g | 0 | 0.5 | 0
branch 90g | 0 | 1 | 0
bend 90 gr | 0 | 3.5 | 0 |  | laminar: 3,5 - turbulent: 0,35
diverter | 0 | 1 | 0
reducer | 0 | 0.1 | 0
inlet | 0 | 1 | 0
filter | 0 | 6 | 0
bellow | 0 | 0.2 | 0
total |  |  | 0

## DN40 S
Calculation pressure loss in liquid pipelines
fill in values
Q = flow of liquid in m3/h |  |  |  | 0 | m3/h
q = specific weight of liquid in kg/m3 |  |  |  | 1025 | kg/m3
Kv = kinematic viscosity in cst |  |  |  | 1 | cst-mm2/s
L = length of straight pipe in m |  |  |  | 0 | m
D = diameter inside in mm |  |  |  | 40 | mm | DN | 40 |  | pipe dimension: | 0 | 1=normal(C100), 2=heavy(C105), 3=extra(C110)
M = material of pipe (1=steel , 2=non steel) |  |  |  | 0 |  | k st | 0.15 | mm | k pvc | 0.02 | mm
S = total of resistant value |  |  |  | 0
Result of calculation :
Velocity : |  |  | V = Q / 3600 / 0.785 x D x D = |  |  |  | 0 | m/sec
Reynolds nr :(>2320 = turb.flow) |  |  | Re = V x D / Kv = |  |  |  | 0 | 0
k/d | [6 empty] | 0.00375
Re.k/d | [6 empty] | 0
Resistant coefficient :(Laminar flow) |  |  | y = 64 / Re = |  |  |  | 0
Resistant coefficient :(Turb. flow) |  |  | y = 0.0055(1+(20000k/D+10^6/Re)^1/3 = |  |  |  | 0
Diff.pressure : |  |  | Dp = (yxL/D+S)xqxVxV/(2x100000) = |  |  |  | 0 | bar | p=rho*g*H
[7 empty] | 0 | m.w.c. | H=p/(rho*g)
check |  |  | hydraulisch glad |  |  |  | ruw |  |  |  | overgangsgebied
|  |  | Re.k/d<65 |  | Re |  | Re.k/d>1300 |  |  |  | 65<Re.k/d<1300
y
|  | 4.58a | #DIV/0! | Blasius | <1e5 | 4.59a | 0.027853 | Nikuradse |  | 4.60 | #DIV/0!
|  | 4.58b | #DIV/0! | Nikuradse | 1e5-5e6 | 4.59b | 0.028804 | Moody
|  | 4.58d | #DIV/0! | Hermann | <2e6
S | amount | zeta | zeta total |  | remark
check vlv | 0 | 5 | 0
but fl vlv | 0 | 0.5 | 0
globe valve | 0 | 4 | 0
flow reg. vlv | 0 | 5 | 0
gate valve | 0 | 0.5 | 0
branch 180g | 0 | 0.5 | 0
branch 90g | 0 | 1 | 0
bend 90 gr | 0 | 3.5 | 0 |  | laminar: 3,5 - turbulent: 0,35
diverter | 0 | 1 | 0
reducer | 0 | 0.1 | 0
inlet | 0 | 1 | 0
filter | 0 | 6 | 0
bellow | 0 | 0.2 | 0
total |  |  | 0

## DN32 S
Calculation pressure loss in liquid pipelines
fill in values
Q = flow of liquid in m3/h |  |  |  | 0 | m3/h
q = specific weight of liquid in kg/m3 |  |  |  | 1025 | kg/m3
Kv = kinematic viscosity in cst |  |  |  | 1 | cst-mm2/s
L = length of straight pipe in m |  |  |  | 0 | m
D = diameter inside in mm |  |  |  | 32 | mm | DN | 32 |  | pipe dimension: | 0 | 1=normal(C100), 2=heavy(C105), 3=extra(C110)
M = material of pipe (1=steel , 2=non steel) |  |  |  | 0 |  | k st | 0.15 | mm | k pvc | 0.02 | mm
S = total of resistant value |  |  |  | 0
Result of calculation :
Velocity : |  |  | V = Q / 3600 / 0.785 x D x D = |  |  |  | 0 | m/sec
Reynolds nr :(>2320 = turb.flow) |  |  | Re = V x D / Kv = |  |  |  | 0 | 0
k/d | [6 empty] | 0.0046875
Re.k/d | [6 empty] | 0
Resistant coefficient :(Laminar flow) |  |  | y = 64 / Re = |  |  |  | 0
Resistant coefficient :(Turb. flow) |  |  | y = 0.0055(1+(20000k/D+10^6/Re)^1/3 = |  |  |  | 0
Diff.pressure : |  |  | Dp = (yxL/D+S)xqxVxV/(2x100000) = |  |  |  | 0 | bar | p=rho*g*H
[7 empty] | 0 | m.w.c. | H=p/(rho*g)
check |  |  | hydraulisch glad |  |  |  | ruw |  |  |  | overgangsgebied
|  |  | Re.k/d<65 |  | Re |  | Re.k/d>1300 |  |  |  | 65<Re.k/d<1300
y
|  | 4.58a | #DIV/0! | Blasius | <1e5 | 4.59a | 0.029746 | Nikuradse |  | 4.60 | #DIV/0!
|  | 4.58b | #DIV/0! | Nikuradse | 1e5-5e6 | 4.59b | 0.030604 | Moody
|  | 4.58d | #DIV/0! | Hermann | <2e6
S | amount | zeta | zeta total |  | remark
check vlv | 0 | 5 | 0
but fl vlv | 0 | 0.5 | 0
globe valve | 0 | 4 | 0
flow reg. vlv | 0 | 5 | 0
gate valve | 0 | 0.5 | 0
branch 180g | 0 | 0.5 | 0
branch 90g | 0 | 1 | 0
bend 90 gr | 0 | 3.5 | 0 |  | laminar: 3,5 - turbulent: 0,35
diverter | 0 | 1 | 0
reducer | 0 | 0.1 | 0
inlet | 0 | 1 | 0
filter | 0 | 6 | 0
bellow | 0 | 0.2 | 0
total |  |  | 0

## DN25 S
Calculation pressure loss in liquid pipelines
fill in values
Q = flow of liquid in m3/h |  |  |  | 0 | m3/h
q = specific weight of liquid in kg/m3 |  |  |  | 1025 | kg/m3
Kv = kinematic viscosity in cst |  |  |  | 1 | cst-mm2/s
L = length of straight pipe in m |  |  |  | 0 | m
D = diameter inside in mm |  |  |  | 25 | mm | DN | 25 |  | pipe dimension: | 0 | 1=normal(C100), 2=heavy(C105), 3=extra(C110)
M = material of pipe (1=steel , 2=non steel) |  |  |  | 0 |  | k st | 0.15 | mm | k pvc | 0.02 | mm
S = total of resistant value |  |  |  | 0
Result of calculation :
Velocity : |  |  | V = Q / 3600 / 0.785 x D x D = |  |  |  | 0 | m/sec
Reynolds nr :(>2320 = turb.flow) |  |  | Re = V x D / Kv = |  |  |  | 0 | 0
k/d | [6 empty] | 0.006
Re.k/d | [6 empty] | 0
Resistant coefficient :(Laminar flow) |  |  | y = 64 / Re = |  |  |  | 0
Resistant coefficient :(Turb. flow) |  |  | y = 0.0055(1+(20000k/D+10^6/Re)^1/3 = |  |  |  | 0
Diff.pressure : |  |  | Dp = (yxL/D+S)xqxVxV/(2x100000) = |  |  |  | 0 | bar | p=rho*g*H
[7 empty] | 0 | m.w.c. | H=p/(rho*g)
check |  |  | hydraulisch glad |  |  |  | ruw |  |  |  | overgangsgebied
|  |  | Re.k/d<65 |  | Re |  | Re.k/d>1300 |  |  |  | 65<Re.k/d<1300
y
|  | 4.58a | #DIV/0! | Blasius | <1e5 | 4.59a | 0.032074 | Nikuradse |  | 4.60 | #DIV/0!
|  | 4.58b | #DIV/0! | Nikuradse | 1e5-5e6 | 4.59b | 0.032757 | Moody
|  | 4.58d | #DIV/0! | Hermann | <2e6
S | amount | zeta | zeta total |  | remark
check vlv | 0 | 5 | 0
but fl vlv | 0 | 0.5 | 0
globe valve | 0 | 4 | 0
flow reg. vlv | 0 | 5 | 0
gate valve | 0 | 0.5 | 0
branch 180g | 0 | 0.5 | 0
branch 90g | 0 | 1 | 0
bend 90 gr | 0 | 3.5 | 0 |  | laminar: 3,5 - turbulent: 0,35
diverter | 0 | 1 | 0
reducer | 0 | 0.1 | 0
inlet | 0 | 1 | 0
filter | 0 | 6 | 0
bellow | 0 | 0.2 | 0
total |  |  | 0

## DN500 P
Calculation pressure loss in liquid pipelines
fill in values
Q = flow of liquid in m3/h |  |  |  | 0 | m3/h
q = specific weight of liquid in kg/m3 |  |  |  | 1025 | kg/m3
Kv = kinematic viscosity in cst |  |  |  | 1 | cst-mm2/s
L = length of straight pipe in m |  |  |  | 0 | m
D = diameter inside in mm |  |  |  | 450 | mm | DN | 450 |  | pipe dimension: | 0 | 1=normal(C100), 2=heavy(C105), 3=extra(C110)
M = material of pipe (1=steel , 2=non steel) |  |  |  | 0 |  | k st | 0.15 | mm | k pvc | 0.02 | mm
S = total of resistant value |  |  |  | 0
Result of calculation :
Velocity : |  |  | V = Q / 3600 / 0.785 x D x D = |  |  |  | 0 | m/sec
Reynolds nr :(>2320 = turb.flow) |  |  | Re = V x D / Kv = |  |  |  | 0 | 0
k/d | [6 empty] | 0.00033333
Re.k/d | [6 empty] | 0
Resistant coefficient :(Laminar flow) |  |  | y = 64 / Re = |  |  |  | 0
Resistant coefficient :(Turb. flow) |  |  | y = 0.0055(1+(20000k/D+10^6/Re)^1/3 = |  |  |  | 0
Diff.pressure : |  |  | Dp = (yxL/D+S)xqxVxV/(2x100000) = |  |  |  | 0 | bar | p=rho*g*H
[7 empty] | 0 | m.w.c. | H=p/(rho*g)
check |  |  | hydraulisch glad |  |  |  | ruw |  |  |  | overgangsgebied
|  |  | Re.k/d<65 |  | Re |  | Re.k/d>1300 |  |  |  | 65<Re.k/d<1300
y
|  | 4.58a | #DIV/0! | Blasius | <1e5 | 4.59a | 0.015263 | Nikuradse |  | 4.60 | #DIV/0!
|  | 4.58b | #DIV/0! | Nikuradse | 1e5-5e6 | 4.59b | 0.0159 | Moody
|  | 4.58d | #DIV/0! | Hermann | <2e6
S | amount | zeta | zeta total |  | remark
check vlv | 0 | 5 | 0
but fl vlv | 0 | 0.5 | 0
globe valve | 0 | 4 | 0
flow reg. vlv | 0 | 5 | 0
gate valve | 0 | 0.5 | 0
branch 180g | 0 | 0.5 | 0
branch 90g | 0 | 1 | 0
bend 90 gr | 0 | 3.5 | 0 |  | laminar: 3,5 - turbulent: 0,35
diverter | 0 | 1 | 0
reducer | 0 | 0.1 | 0
inlet | 0 | 1 | 0
filter | 0 | 6 | 0
bellow | 0 | 0.2 | 0
total |  |  | 0

## DN450 P
Calculation pressure loss in liquid pipelines
fill in values
Q = flow of liquid in m3/h |  |  |  | 0 | m3/h
q = specific weight of liquid in kg/m3 |  |  |  | 1025 | kg/m3
Kv = kinematic viscosity in cst |  |  |  | 1 | cst-mm2/s
L = length of straight pipe in m |  |  |  | 0 | m
D = diameter inside in mm |  |  |  | 450 | mm | DN | 450 |  | pipe dimension: | 0 | 1=normal(C100), 2=heavy(C105), 3=extra(C110)
M = material of pipe (1=steel , 2=non steel) |  |  |  | 0 |  | k st | 0.15 | mm | k pvc | 0.02 | mm
S = total of resistant value |  |  |  | 0
Result of calculation :
Velocity : |  |  | V = Q / 3600 / 0.785 x D x D = |  |  |  | 0 | m/sec
Reynolds nr :(>2320 = turb.flow) |  |  | Re = V x D / Kv = |  |  |  | 0 | 0
k/d | [6 empty] | 0.00033333
Re.k/d | [6 empty] | 0
Resistant coefficient :(Laminar flow) |  |  | y = 64 / Re = |  |  |  | 0
Resistant coefficient :(Turb. flow) |  |  | y = 0.0055(1+(20000k/D+10^6/Re)^1/3 = |  |  |  | 0
Diff.pressure : |  |  | Dp = (yxL/D+S)xqxVxV/(2x100000) = |  |  |  | 0 | bar | p=rho*g*H
[7 empty] | 0 | m.w.c. | H=p/(rho*g)
check |  |  | hydraulisch glad |  |  |  | ruw |  |  |  | overgangsgebied
|  |  | Re.k/d<65 |  | Re |  | Re.k/d>1300 |  |  |  | 65<Re.k/d<1300
y
|  | 4.58a | #DIV/0! | Blasius | <1e5 | 4.59a | 0.015263 | Nikuradse |  | 4.60 | #DIV/0!
|  | 4.58b | #DIV/0! | Nikuradse | 1e5-5e6 | 4.59b | 0.0159 | Moody
|  | 4.58d | #DIV/0! | Hermann | <2e6
S | amount | zeta | zeta total |  | remark
check vlv | 0 | 5 | 0
but fl vlv | 0 | 0.5 | 0
globe valve | 0 | 4 | 0
flow reg. vlv | 0 | 5 | 0
gate valve | 0 | 0.5 | 0
branch 180g | 0 | 0.5 | 0
branch 90g | 0 | 1 | 0
bend 90 gr | 0 | 3.5 | 0 |  | laminar: 3,5 - turbulent: 0,35
diverter | 0 | 1 | 0
reducer | 0 | 0.1 | 0
inlet | 0 | 1 | 0
filter | 0 | 6 | 0
bellow | 0 | 0.2 | 0
total |  |  | 0

## DN400 P
Calculation pressure loss in liquid pipelines
fill in values
Q = flow of liquid in m3/h |  |  |  | 0 | m3/h
q = specific weight of liquid in kg/m3 |  |  |  | 1025 | kg/m3
Kv = kinematic viscosity in cst |  |  |  | 1 | cst-mm2/s
L = length of straight pipe in m |  |  |  | 0 | m
D = diameter inside in mm |  |  |  | 400 | mm | DN | 400 |  | pipe dimension: | 0 | 1=normal(C100), 2=heavy(C105), 3=extra(C110)
M = material of pipe (1=steel , 2=non steel) |  |  |  | 0 |  | k st | 0.15 | mm | k pvc | 0.02 | mm
S = total of resistant value |  |  |  | 0
Result of calculation :
Velocity : |  |  | V = Q / 3600 / 0.785 x D x D = |  |  |  | 0 | m/sec
Reynolds nr :(>2320 = turb.flow) |  |  | Re = V x D / Kv = |  |  |  | 0 | 0
k/d | [6 empty] | 0.000375
Re.k/d | [6 empty] | 0
Resistant coefficient :(Laminar flow) |  |  | y = 64 / Re = |  |  |  | 0
Resistant coefficient :(Turb. flow) |  |  | y = 0.0055(1+(20000k/D+10^6/Re)^1/3 = |  |  |  | 0
Diff.pressure : |  |  | Dp = (yxL/D+S)xqxVxV/(2x100000) = |  |  |  | 0 | bar | p=rho*g*H
[7 empty] | 0 | m.w.c. | H=p/(rho*g)
check |  |  | hydraulisch glad |  |  |  | ruw |  |  |  | overgangsgebied
|  |  | Re.k/d<65 |  | Re |  | Re.k/d>1300 |  |  |  | 65<Re.k/d<1300
y
|  | 4.58a | #DIV/0! | Blasius | <1e5 | 4.59a | 0.015657 | Nikuradse |  | 4.60 | #DIV/0!
|  | 4.58b | #DIV/0! | Nikuradse | 1e5-5e6 | 4.59b | 0.016317 | Moody
|  | 4.58d | #DIV/0! | Hermann | <2e6
S | amount | zeta | zeta total |  | remark
check vlv | 0 | 5 | 0
but fl vlv | 0 | 0.5 | 0
globe valve | 0 | 4 | 0
flow reg. vlv | 0 | 5 | 0
gate valve | 0 | 0.5 | 0
branch 180g | 0 | 0.5 | 0
branch 90g | 0 | 1 | 0
bend 90 gr | 0 | 3.5 | 0 |  | laminar: 3,5 - turbulent: 0,35
diverter | 0 | 1 | 0
reducer | 0 | 0.1 | 0
inlet | 0 | 1 | 0
filter | 0 | 6 | 0
bellow | 0 | 0.2 | 0
total |  |  | 0

## DN350 P
Calculation pressure loss in liquid pipelines
fill in values
Q = flow of liquid in m3/h |  |  |  | 0 | m3/h
q = specific weight of liquid in kg/m3 |  |  |  | 1025 | kg/m3
Kv = kinematic viscosity in cst |  |  |  | 1 | cst-mm2/s
L = length of straight pipe in m |  |  |  | 0 | m
D = diameter inside in mm |  |  |  | 350 | mm | DN | 350 |  | pipe dimension: | 0 | 1=normal(C100), 2=heavy(C105), 3=extra(C110)
M = material of pipe (1=steel , 2=non steel) |  |  |  | 0 |  | k st | 0.15 | mm | k pvc | 0.02 | mm
S = total of resistant value |  |  |  | 0
Result of calculation :
Velocity : |  |  | V = Q / 3600 / 0.785 x D x D = |  |  |  | 0 | m/sec
Reynolds nr :(>2320 = turb.flow) |  |  | Re = V x D / Kv = |  |  |  | 0 | 0
k/d | [6 empty] | 0.00042857
Re.k/d | [6 empty] | 0
Resistant coefficient :(Laminar flow) |  |  | y = 64 / Re = |  |  |  | 0
Resistant coefficient :(Turb. flow) |  |  | y = 0.0055(1+(20000k/D+10^6/Re)^1/3 = |  |  |  | 0
Diff.pressure : |  |  | Dp = (yxL/D+S)xqxVxV/(2x100000) = |  |  |  | 0 | bar | p=rho*g*H
[7 empty] | 0 | m.w.c. | H=p/(rho*g)
check |  |  | hydraulisch glad |  |  |  | ruw |  |  |  | overgangsgebied
|  |  | Re.k/d<65 |  | Re |  | Re.k/d>1300 |  |  |  | 65<Re.k/d<1300
y
|  | 4.58a | #DIV/0! | Blasius | <1e5 | 4.59a | 0.016121 | Nikuradse |  | 4.60 | #DIV/0!
|  | 4.58b | #DIV/0! | Nikuradse | 1e5-5e6 | 4.59b | 0.016809 | Moody
|  | 4.58d | #DIV/0! | Hermann | <2e6
S | amount | zeta | zeta total |  | remark
check vlv | 0 | 5 | 0
but fl vlv | 0 | 0.5 | 0
globe valve | 0 | 4 | 0
flow reg. vlv | 0 | 5 | 0
gate valve | 0 | 0.5 | 0
branch 180g | 0 | 0.5 | 0
branch 90g | 0 | 1 | 0
bend 90 gr | 0 | 3.5 | 0 |  | laminar: 3,5 - turbulent: 0,35
diverter | 0 | 1 | 0
reducer | 0 | 0.1 | 0
inlet | 0 | 1 | 0
filter | 0 | 6 | 0
bellow | 0 | 0.2 | 0
total |  |  | 0

## DN300 P
Calculation pressure loss in liquid pipelines
fill in values
Q = flow of liquid in m3/h |  |  |  | 0 | m3/h
q = specific weight of liquid in kg/m3 |  |  |  | 1025 | kg/m3
Kv = kinematic viscosity in cst |  |  |  | 1 | cst-mm2/s
L = length of straight pipe in m |  |  |  | 0 | m
D = diameter inside in mm |  |  |  | 300 | mm | DN | 300 |  | pipe dimension: | 0 | 1=normal(C100), 2=heavy(C105), 3=extra(C110)
M = material of pipe (1=steel , 2=non steel) |  |  |  | 0 |  | k st | 0.15 | mm | k pvc | 0.02 | mm
S = total of resistant value |  |  |  | 0
Result of calculation :
Velocity : |  |  | V = Q / 3600 / 0.785 x D x D = |  |  |  | 0 | m/sec
Reynolds nr :(>2320 = turb.flow) |  |  | Re = V x D / Kv = |  |  |  | 0 | 0
k/d | [6 empty] | 0.0005
Re.k/d | [6 empty] | 0
Resistant coefficient :(Laminar flow) |  |  | y = 64 / Re = |  |  |  | 0
Resistant coefficient :(Turb. flow) |  |  | y = 0.0055(1+(20000k/D+10^6/Re)^1/3 = |  |  |  | 0
Diff.pressure : |  |  | Dp = (yxL/D+S)xqxVxV/(2x100000) = |  |  |  | 0 | bar | p=rho*g*H
[7 empty] | 0 | m.w.c. | H=p/(rho*g)
check |  |  | hydraulisch glad |  |  |  | ruw |  |  |  | overgangsgebied
|  |  | Re.k/d<65 |  | Re |  | Re.k/d>1300 |  |  |  | 65<Re.k/d<1300
y
|  | 4.58a | #DIV/0! | Blasius | <1e5 | 4.59a | 0.016683 | Nikuradse |  | 4.60 | #DIV/0!
|  | 4.58b | #DIV/0! | Nikuradse | 1e5-5e6 | 4.59b | 0.017406 | Moody
|  | 4.58d | #DIV/0! | Hermann | <2e6
S | amount | zeta | zeta total |  | remark
check vlv | 0 | 5 | 0
but fl vlv | 0 | 0.5 | 0
globe valve | 0 | 4 | 0
flow reg. vlv | 0 | 5 | 0
gate valve | 0 | 0.5 | 0
branch 180g | 0 | 0.5 | 0
branch 90g | 0 | 1 | 0
bend 90 gr | 0 | 3.5 | 0 |  | laminar: 3,5 - turbulent: 0,35
diverter | 0 | 1 | 0
reducer | 0 | 0.1 | 0
inlet | 0 | 1 | 0
filter | 0 | 6 | 0
bellow | 0 | 0.2 | 0
total |  |  | 0

## DN250 P
Calculation pressure loss in liquid pipelines
fill in values
Q = flow of liquid in m3/h |  |  |  | 0 | m3/h
q = specific weight of liquid in kg/m3 |  |  |  | 1025 | kg/m3
Kv = kinematic viscosity in cst |  |  |  | 1 | cst-mm2/s
L = length of straight pipe in m |  |  |  | 0 | m
D = diameter inside in mm |  |  |  | 250 | mm | DN | 250 |  | pipe dimension: | 0 | 1=normal(C100), 2=heavy(C105), 3=extra(C110)
M = material of pipe (1=steel , 2=non steel) |  |  |  | 0 |  | k st | 0.15 | mm | k pvc | 0.02 | mm
S = total of resistant value |  |  |  | 0
Result of calculation :
Velocity : |  |  | V = Q / 3600 / 0.785 x D x D = |  |  |  | 0 | m/sec
Reynolds nr :(>2320 = turb.flow) |  |  | Re = V x D / Kv = |  |  |  | 0 | 0
k/d | [6 empty] | 0.0006
Re.k/d | [6 empty] | 0
Resistant coefficient :(Laminar flow) |  |  | y = 64 / Re = |  |  |  | 0
Resistant coefficient :(Turb. flow) |  |  | y = 0.0055(1+(20000k/D+10^6/Re)^1/3 = |  |  |  | 0
Diff.pressure : |  |  | Dp = (yxL/D+S)xqxVxV/(2x100000) = |  |  |  | 0 | bar | p=rho*g*H
[7 empty] | 0 | m.w.c. | H=p/(rho*g)
check |  |  | hydraulisch glad |  |  |  | ruw |  |  |  | overgangsgebied
|  |  | Re.k/d<65 |  | Re |  | Re.k/d>1300 |  |  |  | 65<Re.k/d<1300
y
|  | 4.58a | #DIV/0! | Blasius | <1e5 | 4.59a | 0.017388 | Nikuradse |  | 4.60 | #DIV/0!
|  | 4.58b | #DIV/0! | Nikuradse | 1e5-5e6 | 4.59b | 0.018151 | Moody
|  | 4.58d | #DIV/0! | Hermann | <2e6
S | amount | zeta | zeta total |  | remark
check vlv | 0 | 5 | 0
but fl vlv | 0 | 0.5 | 0
globe valve | 0 | 4 | 0
flow reg. vlv | 0 | 5 | 0
gate valve | 0 | 0.5 | 0
branch 180g | 0 | 0.5 | 0
branch 90g | 0 | 1 | 0
bend 90 gr | 0 | 3.5 | 0 |  | laminar: 3,5 - turbulent: 0,35
diverter | 0 | 1 | 0
reducer | 0 | 0.1 | 0
inlet | 0 | 1 | 0
filter | 0 | 6 | 0
bellow | 0 | 0.2 | 0
total |  |  | 0

## DN200 P
Calculation pressure loss in liquid pipelines
fill in values
Q = flow of liquid in m3/h |  |  |  | 0 | m3/h
q = specific weight of liquid in kg/m3 |  |  |  | 1025 | kg/m3
Kv = kinematic viscosity in cst |  |  |  | 1 | cst-mm2/s
L = length of straight pipe in m |  |  |  | 0 | m
D = diameter inside in mm |  |  |  | 200 | mm | DN | 200 |  | pipe dimension: | 0 | 1=normal(C100), 2=heavy(C105), 3=extra(C110)
M = material of pipe (1=steel , 2=non steel) |  |  |  | 0 |  | k st | 0.15 | mm | k pvc | 0.02 | mm
S = total of resistant value |  |  |  | 0
Result of calculation :
Velocity : |  |  | V = Q / 3600 / 0.785 x D x D = |  |  |  | 0 | m/sec
Reynolds nr :(>2320 = turb.flow) |  |  | Re = V x D / Kv = |  |  |  | 0 | 0
k/d | [6 empty] | 0.00075
Re.k/d | [6 empty] | 0
Resistant coefficient :(Laminar flow) |  |  | y = 64 / Re = |  |  |  | 0
Resistant coefficient :(Turb. flow) |  |  | y = 0.0055(1+(20000k/D+10^6/Re)^1/3 = |  |  |  | 0
Diff.pressure : |  |  | Dp = (yxL/D+S)xqxVxV/(2x100000) = |  |  |  | 0 | bar | p=rho*g*H
[7 empty] | 0 | m.w.c. | H=p/(rho*g)
check |  |  | hydraulisch glad |  |  |  | ruw |  |  |  | overgangsgebied
|  |  | Re.k/d<65 |  | Re |  | Re.k/d>1300 |  |  |  | 65<Re.k/d<1300
y
|  | 4.58a | #DIV/0! | Blasius | <1e5 | 4.59a | 0.018312 | Nikuradse |  | 4.60 | #DIV/0!
|  | 4.58b | #DIV/0! | Nikuradse | 1e5-5e6 | 4.59b | 0.019128 | Moody
|  | 4.58d | #DIV/0! | Hermann | <2e6
S | amount | zeta | zeta total |  | remark
check vlv | 0 | 5 | 0
but fl vlv | 0 | 0.5 | 0
globe valve | 0 | 4 | 0
flow reg. vlv | 0 | 5 | 0
gate valve | 0 | 0.5 | 0
branch 180g | 0 | 0.5 | 0
branch 90g | 0 | 1 | 0
bend 90 gr | 0 | 3.5 | 0 |  | laminar: 3,5 - turbulent: 0,35
diverter | 0 | 1 | 0
reducer | 0 | 0.1 | 0
inlet | 0 | 1 | 0
filter | 0 | 6 | 0
bellow | 0 | 0.2 | 0
total |  |  | 0

## DN150 P
Calculation pressure loss in liquid pipelines
fill in values
Q = flow of liquid in m3/h |  |  |  | 0 | m3/h
q = specific weight of liquid in kg/m3 |  |  |  | 1025 | kg/m3
Kv = kinematic viscosity in cst |  |  |  | 1 | cst-mm2/s
L = length of straight pipe in m |  |  |  | 0 | m
D = diameter inside in mm |  |  |  | 150 | mm | DN | 150 |  | pipe dimension: | 0 | 1=normal(C100), 2=heavy(C105), 3=extra(C110)
M = material of pipe (1=steel , 2=non steel) |  |  |  | 0 |  | k st | 0.15 | mm | k pvc | 0.02 | mm
S = total of resistant value |  |  |  | 0
Result of calculation :
Velocity : |  |  | V = Q / 3600 / 0.785 x D x D = |  |  |  | 0 | m/sec
Reynolds nr :(>2320 = turb.flow) |  |  | Re = V x D / Kv = |  |  |  | 0 | 0
k/d | [6 empty] | 0.001
Re.k/d | [6 empty] | 0
Resistant coefficient :(Laminar flow) |  |  | y = 64 / Re = |  |  |  | 0
Resistant coefficient :(Turb. flow) |  |  | y = 0.0055(1+(20000k/D+10^6/Re)^1/3 = |  |  |  | 0
Diff.pressure : |  |  | Dp = (yxL/D+S)xqxVxV/(2x100000) = |  |  |  | 0 | bar | p=rho*g*H
[7 empty] | 0 | m.w.c. | H=p/(rho*g)
check |  |  | hydraulisch glad |  |  |  | ruw |  |  |  | overgangsgebied
|  |  | Re.k/d<65 |  | Re |  | Re.k/d>1300 |  |  |  | 65<Re.k/d<1300
y
|  | 4.58a | #DIV/0! | Blasius | <1e5 | 4.59a | 0.019616 | Nikuradse |  | 4.60 | #DIV/0!
|  | 4.58b | #DIV/0! | Nikuradse | 1e5-5e6 | 4.59b | 0.0205 | Moody
|  | 4.58d | #DIV/0! | Hermann | <2e6
S | amount | zeta | zeta total |  | remark
check vlv | 0 | 5 | 0
but fl vlv | 0 | 0.5 | 0
globe valve | 0 | 4 | 0
flow reg. vlv | 0 | 5 | 0
gate valve | 0 | 0.5 | 0
branch 180g | 0 | 0.5 | 0
branch 90g | 0 | 1 | 0
bend 90 gr | 0 | 3.5 | 0 |  | laminar: 3,5 - turbulent: 0,35
diverter | 0 | 1 | 0
reducer | 0 | 0.1 | 0
inlet | 0 | 1 | 0
filter | 0 | 6 | 0
bellow | 0 | 0.2 | 0
total |  |  | 0

## DN125 P
Calculation pressure loss in liquid pipelines
fill in values
Q = flow of liquid in m3/h |  |  |  | 0 | m3/h
q = specific weight of liquid in kg/m3 |  |  |  | 1025 | kg/m3
Kv = kinematic viscosity in cst |  |  |  | 1 | cst-mm2/s
L = length of straight pipe in m |  |  |  | 0 | m
D = diameter inside in mm |  |  |  | 125 | mm | DN | 125 |  | pipe dimension: | 0 | 1=normal(C100), 2=heavy(C105), 3=extra(C110)
M = material of pipe (1=steel , 2=non steel) |  |  |  | 0 |  | k st | 0.15 | mm | k pvc | 0.02 | mm
S = total of resistant value |  |  |  | 0
Result of calculation :
Velocity : |  |  | V = Q / 3600 / 0.785 x D x D = |  |  |  | 0 | m/sec
Reynolds nr :(>2320 = turb.flow) |  |  | Re = V x D / Kv = |  |  |  | 0 | 0
k/d | [6 empty] | 0.0012
Re.k/d | [6 empty] | 0
Resistant coefficient :(Laminar flow) |  |  | y = 64 / Re = |  |  |  | 0
Resistant coefficient :(Turb. flow) |  |  | y = 0.0055(1+(20000k/D+10^6/Re)^1/3 = |  |  |  | 0
Diff.pressure : |  |  | Dp = (yxL/D+S)xqxVxV/(2x100000) = |  |  |  | 0 | bar | p=rho*g*H
[7 empty] | 0 | m.w.c. | H=p/(rho*g)
check |  |  | hydraulisch glad |  |  |  | ruw |  |  |  | overgangsgebied
|  |  | Re.k/d<65 |  | Re |  | Re.k/d>1300 |  |  |  | 65<Re.k/d<1300
y
|  | 4.58a | #DIV/0! | Blasius | <1e5 | 4.59a | 0.020516 | Nikuradse |  | 4.60 | #DIV/0!
|  | 4.58b | #DIV/0! | Nikuradse | 1e5-5e6 | 4.59b | 0.02144 | Moody
|  | 4.58d | #DIV/0! | Hermann | <2e6
S | amount | zeta | zeta total |  | remark
check vlv | 0 | 5 | 0
but fl vlv | 0 | 0.5 | 0
globe valve | 0 | 4 | 0
flow reg. vlv | 0 | 5 | 0
gate valve | 0 | 0.5 | 0
branch 180g | 0 | 0.5 | 0
branch 90g | 0 | 1 | 0
bend 90 gr | 0 | 3.5 | 0 |  | laminar: 3,5 - turbulent: 0,35
diverter | 0 | 1 | 0
reducer | 0 | 0.1 | 0
inlet | 0 | 1 | 0
filter | 0 | 6 | 0
bellow | 0 | 0.2 | 0
total |  |  | 0

## DN100 P
Calculation pressure loss in liquid pipelines
fill in values
Q = flow of liquid in m3/h |  |  |  | 0 | m3/h
q = specific weight of liquid in kg/m3 |  |  |  | 1025 | kg/m3
Kv = kinematic viscosity in cst |  |  |  | 1 | cst-mm2/s
L = length of straight pipe in m |  |  |  | 0 | m
D = diameter inside in mm |  |  |  | 100 | mm | DN | 100 |  | pipe dimension: | 0 | 1=normal(C100), 2=heavy(C105), 3=extra(C110)
M = material of pipe (1=steel , 2=non steel) |  |  |  | 0 |  | k st | 0.15 | mm | k pvc | 0.02 | mm
S = total of resistant value |  |  |  | 0
Result of calculation :
Velocity : |  |  | V = Q / 3600 / 0.785 x D x D = |  |  |  | 0 | m/sec
Reynolds nr :(>2320 = turb.flow) |  |  | Re = V x D / Kv = |  |  |  | 0 | 0
k/d | [6 empty] | 0.0015
Re.k/d | [6 empty] | 0
Resistant coefficient :(Laminar flow) |  |  | y = 64 / Re = |  |  |  | 0
Resistant coefficient :(Turb. flow) |  |  | y = 0.0055(1+(20000k/D+10^6/Re)^1/3 = |  |  |  | 0
Diff.pressure : |  |  | Dp = (yxL/D+S)xqxVxV/(2x100000) = |  |  |  | 0 | bar | p=rho*g*H
[7 empty] | 0 | m.w.c. | H=p/(rho*g)
check |  |  | hydraulisch glad |  |  |  | ruw |  |  |  | overgangsgebied
|  |  | Re.k/d<65 |  | Re |  | Re.k/d>1300 |  |  |  | 65<Re.k/d<1300
y
|  | 4.58a | #DIV/0! | Blasius | <1e5 | 4.59a | 0.021704 | Nikuradse |  | 4.60 | #DIV/0!
|  | 4.58b | #DIV/0! | Nikuradse | 1e5-5e6 | 4.59b | 0.022671 | Moody
|  | 4.58d | #DIV/0! | Hermann | <2e6
S | amount | zeta | zeta total |  | remark
check vlv | 0 | 5 | 0
but fl vlv | 0 | 0.5 | 0
globe valve | 0 | 4 | 0
flow reg. vlv | 0 | 5 | 0
gate valve | 0 | 0.5 | 0
branch 180g | 0 | 0.5 | 0
branch 90g | 0 | 1 | 0
bend 90 gr | 0 | 3.5 | 0 |  | laminar: 3,5 - turbulent: 0,35
diverter | 0 | 1 | 0
reducer | 0 | 0.1 | 0
inlet | 0 | 1 | 0
filter | 0 | 6 | 0
bellow | 0 | 0.2 | 0
total |  |  | 0

## DN80 P
Calculation pressure loss in liquid pipelines
fill in values
Q = flow of liquid in m3/h |  |  |  | 0 | m3/h
q = specific weight of liquid in kg/m3 |  |  |  | 1025 | kg/m3
Kv = kinematic viscosity in cst |  |  |  | 1 | cst-mm2/s
L = length of straight pipe in m |  |  |  | 0 | m
D = diameter inside in mm |  |  |  | 80 | mm | DN | 80 |  | pipe dimension: | 0 | 1=normal(C100), 2=heavy(C105), 3=extra(C110)
M = material of pipe (1=steel , 2=non steel) |  |  |  | 0 |  | k st | 0.15 | mm | k pvc | 0.02 | mm
S = total of resistant value |  |  |  | 0
Result of calculation :
Velocity : |  |  | V = Q / 3600 / 0.785 x D x D = |  |  |  | 0 | m/sec
Reynolds nr :(>2320 = turb.flow) |  |  | Re = V x D / Kv = |  |  |  | 0 | 0
k/d | [6 empty] | 0.001875
Re.k/d | [6 empty] | 0
Resistant coefficient :(Laminar flow) |  |  | y = 64 / Re = |  |  |  | 0
Resistant coefficient :(Turb. flow) |  |  | y = 0.0055(1+(20000k/D+10^6/Re)^1/3 = |  |  |  | 0
Diff.pressure : |  |  | Dp = (yxL/D+S)xqxVxV/(2x100000) = |  |  |  | 0 | bar | p=rho*g*H
[7 empty] | 0 | m.w.c. | H=p/(rho*g)
check |  |  | hydraulisch glad |  |  |  | ruw |  |  |  | overgangsgebied
|  |  | Re.k/d<65 |  | Re |  | Re.k/d>1300 |  |  |  | 65<Re.k/d<1300
y
|  | 4.58a | #DIV/0! | Blasius | <1e5 | 4.59a | 0.022999 | Nikuradse |  | 4.60 | #DIV/0!
|  | 4.58b | #DIV/0! | Nikuradse | 1e5-5e6 | 4.59b | 0.023997 | Moody
|  | 4.58d | #DIV/0! | Hermann | <2e6
S | amount | zeta | zeta total |  | remark
check vlv | 0 | 5 | 0
but fl vlv | 0 | 0.5 | 0
globe valve | 0 | 4 | 0
flow reg. vlv | 0 | 5 | 0
gate valve | 0 | 0.5 | 0
branch 180g | 0 | 0.5 | 0
branch 90g | 0 | 1 | 0
bend 90 gr | 0 | 3.5 | 0 |  | laminar: 3,5 - turbulent: 0,35
diverter | 0 | 1 | 0
reducer | 0 | 0.1 | 0
inlet | 0 | 1 | 0
filter | 0 | 6 | 0
bellow | 0 | 0.2 | 0
total |  |  | 0

## DN65 P
Calculation pressure loss in liquid pipelines
fill in values
Q = flow of liquid in m3/h |  |  |  | 0 | m3/h
q = specific weight of liquid in kg/m3 |  |  |  | 1025 | kg/m3
Kv = kinematic viscosity in cst |  |  |  | 1 | cst-mm2/s
L = length of straight pipe in m |  |  |  | 0 | m
D = diameter inside in mm |  |  |  | 65 | mm | DN | 65 |  | pipe dimension: | 0 | 1=normal(C100), 2=heavy(C105), 3=extra(C110)
M = material of pipe (1=steel , 2=non steel) |  |  |  | 0 |  | k st | 0.15 | mm | k pvc | 0.02 | mm
S = total of resistant value |  |  |  | 0
Result of calculation :
Velocity : |  |  | V = Q / 3600 / 0.785 x D x D = |  |  |  | 0 | m/sec
Reynolds nr :(>2320 = turb.flow) |  |  | Re = V x D / Kv = |  |  |  | 0 | 0
k/d | [6 empty] | 0.0023077
Re.k/d | [6 empty] | 0
Resistant coefficient :(Laminar flow) |  |  | y = 64 / Re = |  |  |  | 0
Resistant coefficient :(Turb. flow) |  |  | y = 0.0055(1+(20000k/D+10^6/Re)^1/3 = |  |  |  | 0
Diff.pressure : |  |  | Dp = (yxL/D+S)xqxVxV/(2x100000) = |  |  |  | 0 | bar | p=rho*g*H
[7 empty] | 0 | m.w.c. | H=p/(rho*g)
check |  |  | hydraulisch glad |  |  |  | ruw |  |  |  | overgangsgebied
|  |  | Re.k/d<65 |  | Re |  | Re.k/d>1300 |  |  |  | 65<Re.k/d<1300
y
|  | 4.58a | #DIV/0! | Blasius | <1e5 | 4.59a | 0.02431 | Nikuradse |  | 4.60 | #DIV/0!
|  | 4.58b | #DIV/0! | Nikuradse | 1e5-5e6 | 4.59b | 0.025322 | Moody
|  | 4.58d | #DIV/0! | Hermann | <2e6
S | amount | zeta | zeta total |  | remark
check vlv | 0 | 5 | 0
but fl vlv | 0 | 0.5 | 0
globe valve | 0 | 4 | 0
flow reg. vlv | 0 | 5 | 0
gate valve | 0 | 0.5 | 0
branch 180g | 0 | 0.5 | 0
branch 90g | 0 | 1 | 0
bend 90 gr | 0 | 3.5 | 0 |  | laminar: 3,5 - turbulent: 0,35
diverter | 0 | 1 | 0
reducer | 0 | 0.1 | 0
inlet | 0 | 1 | 0
filter | 0 | 6 | 0
bellow | 0 | 0.2 | 0
total |  |  | 0

## DN50 P
Calculation pressure loss in liquid pipelines
fill in values
Q = flow of liquid in m3/h |  |  |  | 0 | m3/h
q = specific weight of liquid in kg/m3 |  |  |  | 1025 | kg/m3
Kv = kinematic viscosity in cst |  |  |  | 1 | cst-mm2/s
L = length of straight pipe in m |  |  |  | 0 | m
D = diameter inside in mm |  |  |  | 50 | mm | DN | 50 |  | pipe dimension: | 0 | 1=normal(C100), 2=heavy(C105), 3=extra(C110)
M = material of pipe (1=steel , 2=non steel) |  |  |  | 0 |  | k st | 0.15 | mm | k pvc | 0.02 | mm
S = total of resistant value |  |  |  | 0
Result of calculation :
Velocity : |  |  | V = Q / 3600 / 0.785 x D x D = |  |  |  | 0 | m/sec
Reynolds nr :(>2320 = turb.flow) |  |  | Re = V x D / Kv = |  |  |  | 0 | 0
k/d | [6 empty] | 0.003
Re.k/d | [6 empty] | 0
Resistant coefficient :(Laminar flow) |  |  | y = 64 / Re = |  |  |  | 0
Resistant coefficient :(Turb. flow) |  |  | y = 0.0055(1+(20000k/D+10^6/Re)^1/3 = |  |  |  | 0
Diff.pressure : |  |  | Dp = (yxL/D+S)xqxVxV/(2x100000) = |  |  |  | 0 | bar | p=rho*g*H
[7 empty] | 0 | m.w.c. | H=p/(rho*g)
check |  |  | hydraulisch glad |  |  |  | ruw |  |  |  | overgangsgebied
|  |  | Re.k/d<65 |  | Re |  | Re.k/d>1300 |  |  |  | 65<Re.k/d<1300
y
|  | 4.58a | #DIV/0! | Blasius | <1e5 | 4.59a | 0.026135 | Nikuradse |  | 4.60 | #DIV/0!
|  | 4.58b | #DIV/0! | Nikuradse | 1e5-5e6 | 4.59b | 0.027134 | Moody
|  | 4.58d | #DIV/0! | Hermann | <2e6
S | amount | zeta | zeta total |  | remark
check vlv | 0 | 5 | 0
but fl vlv | 0 | 0.5 | 0
globe valve | 0 | 4 | 0
flow reg. vlv | 0 | 5 | 0
gate valve | 0 | 0.5 | 0
branch 180g | 0 | 0.5 | 0
branch 90g | 0 | 1 | 0
bend 90 gr | 0 | 3.5 | 0 |  | laminar: 3,5 - turbulent: 0,35
diverter | 0 | 1 | 0
reducer | 0 | 0.1 | 0
inlet | 0 | 1 | 0
filter | 0 | 6 | 0
bellow | 0 | 0.2 | 0
total |  |  | 0

## DN40 P
Calculation pressure loss in liquid pipelines
fill in values
Q = flow of liquid in m3/h |  |  |  | 0 | m3/h
q = specific weight of liquid in kg/m3 |  |  |  | 1025 | kg/m3
Kv = kinematic viscosity in cst |  |  |  | 1 | cst-mm2/s
L = length of straight pipe in m |  |  |  | 0 | m
D = diameter inside in mm |  |  |  | 40 | mm | DN | 40 |  | pipe dimension: | 0 | 1=normal(C100), 2=heavy(C105), 3=extra(C110)
M = material of pipe (1=steel , 2=non steel) |  |  |  | 0 |  | k st | 0.15 | mm | k pvc | 0.02 | mm
S = total of resistant value |  |  |  | 0
Result of calculation :
Velocity : |  |  | V = Q / 3600 / 0.785 x D x D = |  |  |  | 0 | m/sec
Reynolds nr :(>2320 = turb.flow) |  |  | Re = V x D / Kv = |  |  |  | 0 | 0
k/d | [6 empty] | 0.00375
Re.k/d | [6 empty] | 0
Resistant coefficient :(Laminar flow) |  |  | y = 64 / Re = |  |  |  | 0
Resistant coefficient :(Turb. flow) |  |  | y = 0.0055(1+(20000k/D+10^6/Re)^1/3 = |  |  |  | 0
Diff.pressure : |  |  | Dp = (yxL/D+S)xqxVxV/(2x100000) = |  |  |  | 0 | bar | p=rho*g*H
[7 empty] | 0 | m.w.c. | H=p/(rho*g)
check |  |  | hydraulisch glad |  |  |  | ruw |  |  |  | overgangsgebied
|  |  | Re.k/d<65 |  | Re |  | Re.k/d>1300 |  |  |  | 65<Re.k/d<1300
y
|  | 4.58a | #DIV/0! | Blasius | <1e5 | 4.59a | 0.027853 | Nikuradse |  | 4.60 | #DIV/0!
|  | 4.58b | #DIV/0! | Nikuradse | 1e5-5e6 | 4.59b | 0.028804 | Moody
|  | 4.58d | #DIV/0! | Hermann | <2e6
S | amount | zeta | zeta total |  | remark
check vlv | 0 | 5 | 0
but fl vlv | 0 | 0.5 | 0
globe valve | 0 | 4 | 0
flow reg. vlv | 0 | 5 | 0
gate valve | 0 | 0.5 | 0
branch 180g | 0 | 0.5 | 0
branch 90g | 0 | 1 | 0
bend 90 gr | 0 | 3.5 | 0 |  | laminar: 3,5 - turbulent: 0,35
diverter | 0 | 1 | 0
reducer | 0 | 0.1 | 0
inlet | 0 | 1 | 0
filter | 0 | 6 | 0
bellow | 0 | 0.2 | 0
total |  |  | 0

## DN32 P
Calculation pressure loss in liquid pipelines
fill in values
Q = flow of liquid in m3/h |  |  |  | 0 | m3/h
q = specific weight of liquid in kg/m3 |  |  |  | 1025 | kg/m3
Kv = kinematic viscosity in cst |  |  |  | 1 | cst-mm2/s
L = length of straight pipe in m |  |  |  | 0 | m
D = diameter inside in mm |  |  |  | 32 | mm | DN | 32 |  | pipe dimension: | 0 | 1=normal(C100), 2=heavy(C105), 3=extra(C110)
M = material of pipe (1=steel , 2=non steel) |  |  |  | 0 |  | k st | 0.15 | mm | k pvc | 0.02 | mm
S = total of resistant value |  |  |  | 0
Result of calculation :
Velocity : |  |  | V = Q / 3600 / 0.785 x D x D = |  |  |  | 0 | m/sec
Reynolds nr :(>2320 = turb.flow) |  |  | Re = V x D / Kv = |  |  |  | 0 | 0
k/d | [6 empty] | 0.0046875
Re.k/d | [6 empty] | 0
Resistant coefficient :(Laminar flow) |  |  | y = 64 / Re = |  |  |  | 0
Resistant coefficient :(Turb. flow) |  |  | y = 0.0055(1+(20000k/D+10^6/Re)^1/3 = |  |  |  | 0
Diff.pressure : |  |  | Dp = (yxL/D+S)xqxVxV/(2x100000) = |  |  |  | 0 | bar | p=rho*g*H
[7 empty] | 0 | m.w.c. | H=p/(rho*g)
check |  |  | hydraulisch glad |  |  |  | ruw |  |  |  | overgangsgebied
|  |  | Re.k/d<65 |  | Re |  | Re.k/d>1300 |  |  |  | 65<Re.k/d<1300
y
|  | 4.58a | #DIV/0! | Blasius | <1e5 | 4.59a | 0.029746 | Nikuradse |  | 4.60 | #DIV/0!
|  | 4.58b | #DIV/0! | Nikuradse | 1e5-5e6 | 4.59b | 0.030604 | Moody
|  | 4.58d | #DIV/0! | Hermann | <2e6
S | amount | zeta | zeta total |  | remark
check vlv | 0 | 5 | 0
but fl vlv | 0 | 0.5 | 0
globe valve | 0 | 4 | 0
flow reg. vlv | 0 | 5 | 0
gate valve | 0 | 0.5 | 0
branch 180g | 0 | 0.5 | 0
branch 90g | 0 | 1 | 0
bend 90 gr | 0 | 3.5 | 0 |  | laminar: 3,5 - turbulent: 0,35
diverter | 0 | 1 | 0
reducer | 0 | 0.1 | 0
inlet | 0 | 1 | 0
filter | 0 | 6 | 0
bellow | 0 | 0.2 | 0
total |  |  | 0

## DN25 P
Calculation pressure loss in liquid pipelines
fill in values
Q = flow of liquid in m3/h |  |  |  | 0 | m3/h
q = specific weight of liquid in kg/m3 |  |  |  | 1025 | kg/m3
Kv = kinematic viscosity in cst |  |  |  | 1 | cst-mm2/s
L = length of straight pipe in m |  |  |  | 0 | m
D = diameter inside in mm |  |  |  | 25 | mm | DN | 25 |  | pipe dimension: | 0 | 1=normal(C100), 2=heavy(C105), 3=extra(C110)
M = material of pipe (1=steel , 2=non steel) |  |  |  | 0 |  | k st | 0.15 | mm | k pvc | 0.02 | mm
S = total of resistant value |  |  |  | 0
Result of calculation :
Velocity : |  |  | V = Q / 3600 / 0.785 x D x D = |  |  |  | 0 | m/sec
Reynolds nr :(>2320 = turb.flow) |  |  | Re = V x D / Kv = |  |  |  | 0 | 0
k/d | [6 empty] | 0.006
Re.k/d | [6 empty] | 0
Resistant coefficient :(Laminar flow) |  |  | y = 64 / Re = |  |  |  | 0
Resistant coefficient :(Turb. flow) |  |  | y = 0.0055(1+(20000k/D+10^6/Re)^1/3 = |  |  |  | 0
Diff.pressure : |  |  | Dp = (yxL/D+S)xqxVxV/(2x100000) = |  |  |  | 0 | bar | p=rho*g*H
[7 empty] | 0 | m.w.c. | H=p/(rho*g)
check |  |  | hydraulisch glad |  |  |  | ruw |  |  |  | overgangsgebied
|  |  | Re.k/d<65 |  | Re |  | Re.k/d>1300 |  |  |  | 65<Re.k/d<1300
y
|  | 4.58a | #DIV/0! | Blasius | <1e5 | 4.59a | 0.032074 | Nikuradse |  | 4.60 | #DIV/0!
|  | 4.58b | #DIV/0! | Nikuradse | 1e5-5e6 | 4.59b | 0.032757 | Moody
|  | 4.58d | #DIV/0! | Hermann | <2e6
S | amount | zeta | zeta total |  | remark
check vlv | 0 | 5 | 0
but fl vlv | 0 | 0.5 | 0
globe valve | 0 | 4 | 0
flow reg. vlv | 0 | 5 | 0
gate valve | 0 | 0.5 | 0
branch 180g | 0 | 0.5 | 0
branch 90g | 0 | 1 | 0
bend 90 gr | 0 | 3.5 | 0 |  | laminar: 3,5 - turbulent: 0,35
diverter | 0 | 1 | 0
reducer | 0 | 0.1 | 0
inlet | 0 | 1 | 0
filter | 0 | 6 | 0
bellow | 0 | 0.2 | 0
total |  |  | 0

## pipe dimensions
DN | NORMAL | HEAVY | EXTRA
15 | 14.9 | 14.9
20 | 20.5 | 20.5 | 16.9
25 | 26.5 | 26.5 | 23.7
32 | 37.2 | 32.4 | 29.8
40 | 43.1 | 38.3 | 35.7
50 | 54.5 | 50.3 | 47.7
65 | 70.3 | 66.1 | 61.9
80 | 82.5 | 78.9 | 73.7
100 | 107.1 | 104.3 | 97.1
125 | 131.7 | 128.5 | 123.7
150 | 159.3 | 157.1 | 150.7
200 | 206.5 | 206.5 | 199.1
250 | 260.4 | 260.4 | 254.4
300 | 309.7 | 309.7 | 304.9
350 | 339.6 | 339.6 | 336.6
400 | 390.6 | 390.6 | 387.4
450 | 441.2 | 441.2 | 438
500 | 489 | 489 | 489
550 | 540 | 540 | 540
600 | 591 | 591 | 591